## Points_IO_Schedule
ZONE TEMPERATURE AND FAN CONTROL UNIT
POINTS / I/O SCHEDULE
Project | Single-Zone HVAC Control Prototype
Controller | ESP32-S3
Document No. | 1
Revision | 1
Date | 2026-09-24
Prepared By | Nosherwan Saeed
Point ID | Point Description | Point Type | Device | Signal / Interface | Controller Pin | Engineering Unit | Range / State | Normal State | Description
ZN-T-01 | Zone Temperature | AI | DHT22 | Digital | GPIO18 | °C | Application Measurement | Valid Reading | Zone air temperature used for fan control
ZN-H-01 | Zone Relative Humidity | AI | DHT22 | Digital | GPIO18 | %RH | 0–100% | Valid Reading | Zone relative humidity for Monitoring only
ZN-SP-01 | Zone Temperature Setpoint | AI | 10k Potentiometer | ADC | GPIO1 / ADC1_CH0 | °C | 15–30°C | Operator Adjustable | Operator Adjustable temperature setpoint
FAN-01-CMD | Fan Enable Command | DO | Relay Module | Digital, Active-Low | GPIO4 | — | ON/OFF | OFF | Commands fan through relay
STAT-FAN-CMD | Fan Command Active | DO | Green LED | Digital | GPIO5 | — | ON/OFF | OFF | Indicates active fan command
STAT-SAT | Setpoint Satisfied | DO | Yellow LED | Digital | GPIO6 | — | ON/OFF | OFF | Temperature within ±0.5°C of setpoint
STAT-ALM | High Temperature Deviation Alarm | DO | Red LED | Digital | GPIO7 | — | Normal/Alarm | Normal | Temperature exceeds setpoint by >5°C

## Point_Definitions
ZONE TEMPERATURE AND FAN CONTROL UNIT
POINT DEFINITIONS / CONTROL LOGIC
Project | Single-Zone HVAC Control Prototype
Controller | ESP32-S3
Document No. | 1
Revision | 1
Prepared By | Nosherwan Saeed
Point ID | Definition / Control Logic
ZN-T-01 | Temperature measured by the DHT22 and used as the primary control variable for fan operation.
ZN-H-01 | Relative humidity measured by the DHT22 for monitoring purposes. It does not currently affect fan control.
ZN-SP-01 | Setpoint generated from the potentiometer. ADC input is mapped linearly to 15–30°C.
FAN-01-CMD | Fan command generated by the controller. Relay control is active-low: GPIO4 LOW energizes the relay and GPIO4 HIGH de-energizes it.
STAT-FAN-CMD | Green LED follows the controller's fan command state. It does not provide physical fan feedback.
STAT-SAT | Yellow LED is ON when zone temperature is within ±0.5°C of the valid setpoint.
STAT-ALM | Red LED is ON when zone temperature is more than 5°C above the valid setpoint.